Harvard University Technology Standards

System Integration Guideline

Integrated Automation

Revised:  November 27, 2022

Version 1.3

- Table of Contents

1.	Purpose of this Document	6

2.	Questions this Document Will Address:	6

3.	System Types Included	7

4.	Scope Definitions	7

5.	Project Role Definitions	8

6.	Technical Definitions	9

7.	Abbreviations and Acronyms	12

8.	Supporting Resources	14

9.	Preferred Vendors	15

10.	Selecting the Appropriate Specifying Division	16

11.	Specification Level of Detail	16

12.	Specifier’s Responsibilities	17

13.	System Integrator’s Responsibilities	19

14.	Scope of Responsibilities Matrix	20

15.	Integrator Submittals	21

16.	ISC/OT Network Labelling and Asset Management	27

17.	System Commissioning & Demonstration Requirements	27

18.	Warrantee and Service Contract	29

19.	Custom Software & Programming	31

20.	Single Source of Truth	32

21.	Integration Failure Modes	32

22.	Life Safety and Code Compliance	33

23.	Network Operations	33

24.	Operation Technology / ICS Cybersecurity	33

25.	Vendor Provided Network Hardware	34

26.	Vendor Provided Servers	35

27.	Use of Wireless Communications to Support Integrations	36

28.	Remote Access	37

29.	Related Specification Sections	37

30.	Unique Specification Section Requirements	40

| VERSION # | IMPLEMENTED BY | REVISION DATE | APPROVED BY | APPROVAL DATE | REVISIONS/COMMENTS |
| --- | --- | --- | --- | --- | --- |
| 1.0 | Bala Consulting Engineers | 03.29.2022 | TBD | TBD | First Revision |
| 1.1 | Bala Consulting Engineers | 09.15.2022 | TBD | TBD | Minor formatting and updates based on vendor comments |
| 1.1a | Bala Consulting Engineers | 09.15.2022 | TBD | TBD | All internal comments and action items removed for formal distribution. Track changes turned off. |
| 1.2 | Bala Consulting Engineers | 11.11.2022 | TBD | TBD | Prior comments addressed and remaining comments removed |
| 1.2a | Bala Consulting Engineers | 11.11.2022 | TBD | TBD | All internal comments and action items removed for formal distribution. Track changes turned off. |
| 1.3 | Bala Consulting Engineers | 11.27.2022 | TBD | TBD | HUIT reference materials and link revised |
| 1.3a | Bala Consulting Engineers | 11.27.2022 | TBD | TBD | All internal comments and action items removed for formal distribution. Track changes turned off. |

# Purpose of this Document

- To provide guidance to Harvard University’s minimum standards and recommended best practices for Integrated Automation of Operations Technology and Industrial Control systems design and implementation.

- This document outlines a process for identifying, tailoring, and implementing selected integrations.

- This document must be used by design and engineering consultants to supplement their traditional specification of the following systems above. It is imperative that certain aspects of this document are incorporated into a traditional specification produced by design and engineering consultants.

- This document must be used by OT contractors and ICS vendors to tailor their work to meet the expectations of Harvard University. During the design phase and RFP process, enough detail is given to price Harvard University specific alarm strategies, reports, and graphics development, but often certain nuances inherent in each integrated ICS/OT are not defined well enough to execute these tasks. This document will define those nuances and ultimately provide Harvard University with a finished product that meets expectations.

- It must be understood that design and integration professionals who deviate from the process and requirements outlined in this document without obtaining prior written approval from the relevant OT Owner, HU Executive OT Steering Committee AND Business Owner do so at risk of decertification of the platform and/or restriction of integration data services.

  - Where recommendations or requirements in this document conflict with established existing Harvard University practices, means and methods or typical levels of fitout - confirmation of the procedures listed in this document should be requested with the goal of addressing conflicts in a way that meets the intent of the requirement without adding significant cost or burden to the project.

# Questions this Document Will Address:

- Which ICS/OT Vendors must be used for new construction, retrofit, or buildings with mixed ICS/OT platforms?

- Expectations for A/E design firms when designing an ICS/OT Systems for Harvard University:

  - Drawing requirements.

    - Network diagram of all ICS/OT systems and their interconnections (Reference Artlab diagram)

    - Provide a data flow of the application software and system components are used within the ICS/OT Systems to the field level devices.  As well any other ICS/OT interconnections between each system.

  - Use of BACnet standard point naming conventions provided by Harvard University.

    - Point naming is currently not a global standard. Request project specific point naming information from HUIT at othelp@harvard.edu

  - Sequences of Operation.

  - Scope matrix for use by Construction Manager.

  - Coordination completeness

- Expectations for ICS/OT contractors when implementing at Harvard University:

  - Active participation in the full ICS/OT deployment process outlined in this document including participation in a security assessment of the proposed solution and the cyber security practices of the contractor.

  - Hardware design

  - Network design

  - Software design

  - Submittals

  - Installation

  - Commissioning including:

    - Installation verification

    - Start-up testing

    - Operational verification including:

      - System tests

      - Integrated system tests

      - Training

    - Expectations for Commissioning Authority (CxA) when testing ICS/OT:

      - Pre-requisites from ICS/OT contractors.

# System Types Included

Harvard University’s Operational Technology (OT) systems and Industrial Control (ICS) consists of the following, but not limited to:

  - Physical Access Control (access, video, intercom, duress, blue light, etc.)

  - Building Management Systems

  - Chilled Water Plants

  - Distributed Electrical Facility

  - Electric Metering

  - Electronic key management system

  - High Efficiency Energy Recovery System

  - Air Quality Systems

  - Kitchen and Lab Fume Hoods

  - Heating Hot Water Plants

  - Irrigation Systems

  - Lighting Systems

  - Photovoltaic (PV) Cells (Solar Panels)

  - Refrigeration Systems

  - Steam Plants

  - Transportation Systems

  - Space Management & Occupancy Sensing (when installed as standalone)

  - Audiovisual Systems (where integration is required with other systems)

# Scope Definitions

- The following definitions of terms are understood to indicate specific  responsibilities for a scope of work.

  - Provide:  As used herein must mean furnish, install, and test complete.

  - Infrastructure:  As used herein must mean cable, conduit, and raceway with all required boxes, fittings, connectors, and accessories; completely installed.

  - Work:  As used herein must be understood to mean the materials completely installed, including the labor involved to meet the design intent.

- Certain non-technical words and phrases must be understood to have specific meanings as follows:

  - “As indicated” – As shown on, and/or in accordance with, the Documents.

  - “Coordinate” means that Contractor will, while providing any scope of work or specific task, communicate, cooperate and collaborate with all associated trades, vendors and project team members whose products and services have a direct impact on the ability of contractor to deliver this scope. Coordination includes communicating, cooperating, and collaborating to organize the scheduling and performance of the scope of work. Contractor will inform the Owner of occurrences in which any responsibly party fails to communicate, cooperate, or collaborate with Contractor relating to the performance of the scope of work.

  - “Furnish” – Purchase and deliver to the project site complete with every necessary appurtenance and support, all as part of the Work. Purchasing must include payment of any surcharges as may be required to assure that purchased items are free of all liens, claims, or encumbrances.

  - “Install” – Unload at the delivery point at the site and perform every operation necessary to establish secure mounting and correct operation at the proper location in the project, all as part of the Work.

  - “New” – Manufactured within the past year and never before used.

  - “Relocate existing” – Remove existing item from present location. Reinstall, re- connect, and test existing item and make ready for use at new location as indicated.

  - “Remove existing “– Remove existing item and return item to Owner.

  - “Replace” – Remove existing item and return item to Owner. Provide new item as indicated.

# Project Role Definitions

- Design Professional: The Design Professional, or Consultant, is the designer of record for and portion of the ISC/OT system that is retained by the Owner to perform design services for the project.

- Integration: Integration is the act of bringing together smaller components into a single system that functions as one. For the purposes of this document, it is understood that integrated systems are also systems manufactured for different purposes or by different vendors and as such require an interconnection and configuration process to successfully share data and “function as one.”

- Integrator, Systems Integrator: An individual or entity who manages the process by which disparate systems are Integrated. An integrator is typically responsible for furnishing or installing some or all of the components which are to be integrated with and often is required to work with a separate team of integrators responsible for additional building systems/components.

- Master Systems Integrator: An individual or entity, contracted separately from the Division 23, 26, 27 & 28 manufacturers/vendors/contractors who is responsible for providing a central integration platform to tie the individual sub-systems together

  - This entity is not required on all projects and, when required due to the scale or complexity of the integration requirements, is the party directly contracted to the Division 25 specification

  - The determination of the need to include a master systems integrator as part of  the project requirements must be made by the Business Owners and HUIT in consultation with the specifying engineer

- Specifying Engineer (see Design Professional): Designer or engineer responsible for identifying, documenting, and validating integration requirements

  - In most cases, the specifying engineer is not a single entity but multiple designers or engineers from multiple trades (Mechanical, electrical, IT, AV, security, etc.) working in concert. For the purposes of this document “Specifying engineer” must mean all designers or engineers responsible for an integration.

# Technical Definitions

- Algorithm: A logical procedure for solving a recurrent mathematical problem. A prescribed set of well-defined rules or processes for solving a problem in a finite number of steps.

- Analog: A continuously varying signal value, such as current, flow, pressure, or temperature.

- BACnet Specific Definitions:

  - BACnet: Building Automation Control Network Protocol, ASHRAE 135. A communications protocol allowing devices to communicate data and services over a network.

  - BACnet Interoperability Building Blocks (BIBBs): BIBB defines a small portion of BACnet functionality that is needed to perform a particular task. BIBBs are combined to build the BACnet functional requirements for a device.

  - BACnet/IP: Defines and allows using a reserved UDP socket to transmit BACnet messages over IP networks. A BACnet/IP network is a collection of one or more IP subnetworks that share the same BACnet network number.

  - BACnet Testing Laboratories (BTL): Organization responsible for testing products for compliance with ASHRAE 135, operated under direction of BACnet International.

  - Protocol Implementation Conformance Statement (PICS): All devices conforming to the BACnet protocol must have a Protocol Implementation Conformance Statement (PICS) that identifies all of the portions of BACnet that are implemented.

- Bluetooth Lower Energy (Bluetooth LE, BLE): Bluetooth Low Energy is a power-conserving variant of Bluetooth personal area network (PAN) technology, designed for use by Internet-connected machines and appliances.

- Binary: Two-state signal where a high signal level represents "ON" or "OPEN" condition and a low signal level represents "OFF" or "CLOSED" condition. "Digital" is sometimes used interchangeably with "Binary" to indicate a two-state signal.

- Circuit: Any specific run of circuitry.

- Circuitry – Any Work which consists of wires, cables, raceways, and/or specialty wiring method assemblies complete with associated junction boxes, pull boxes, outlet boxes, joints, couplings, splices, and connections except where limited to a lesser meaning by specific description.

- Controller: Generic term for any standalone, microprocessor-based, digital controller residing on a network, used for local or global control. Three types of controllers are indicated: network controllers, programmable application controllers, and application-specific controllers.

- Control System Integrator: An entity that assists in expansion of existing enterprise system and support of additional operator interfaces to I/O being added to existing enterprise system.

- Data: For the purposes of this document, data includes facts, figures or information obtained by one platform which is then requested to be read or written to by a secondary platform via integration.

  - Read – to collect but not have the ability to alter a piece of data

  - Write – to have the ability to read and alter a piece of data

- DDC System Provider: Authorized representative of, and trained by, DDC system manufacturer and responsible for execution of DDC system Work indicated.

- Distributed Control: Processing of system data is decentralized and control decisions are made at subsystem level. System operational programs and information are provided to remote subsystems and status is reported back. On loss of communication, subsystems to be capable of operating in a standalone mode using the last best available data.

- E/P: Voltage to pneumatic.

- Firewall: A part of a computer system or network which is designed to block unauthorized access while permitting outward communication based on an organization's previously established security policies.

- Gateway: Bidirectional protocol translator that connects control systems that use different communication protocols.

- Harvard University IT (HUIT): Organization within Harvard University responsible for setting OT network standards, approving deployment, and managing the Harvard University managed OT networks

- IEC 62443: IEC 62443 is an international series of standards that address cybersecurity for operational technology in automation and control systems. The standard is divided into different sections and describes both technical and process-related aspects of automation and control systems cybersecurity.

- I/O: System through which information is received and transmitted. I/O refers to analog input (AI), binary input (BI), analog output (AO) and binary output (BO). Analog signals are continuous and represent control influences such as flow, level, moisture, pressure, and temperature. Binary signals convert electronic signals to digital pulses (values) and generally represent two-position operating and alarm status. "Digital," (DI) and (DO), is sometimes used interchangeably with "Binary," (BI) and (BO), respectively.

- I/P: Current to pneumatic.

- Internet of Things (IoT): The Internet of Things (IoT) describes the network of physical objects— “things”—that are embedded with sensors, software, and other technologies for the purpose of connecting and exchanging data with other devices and systems over the internet

- LON Specific Definitions:

  - FTT-10: Echelon Transmitter-Free Topology Transceiver.

  - LonMark International: Association comprising suppliers and installers of LonTalk products. Association provides guidelines for implementing LonTalk protocol to ensure interoperability through a standard or consistent implementation.

  - LonTalk: An open standard protocol developed by Echelon Corporation that uses a "Neuron Chip" for communication. LonTalk is a register trademark of Echelon.

  - LonWorks: Network technology developed by Echelon.

  - Node: Device that communicates using CTA-709.1-D protocol and that is connected to a CTA-709.1-D network.

  - Node Address: The logical address of a node on the network, consisting of a Domain number, Subnet number, and Node number. "Node number" portion of an address is a number assigned to device during installation, is unique within a subnet, and is not a factory-set unique Node ID.

  - Node ID: A unique 48-bit identifier assigned at factory to each CTA-709.1-D device. Sometimes called a "Neuron ID."

  - Program ID: An identifier (number) stored in a device (usually, EEPROM) that identifies node manufacturer, functionality of device (application and sequence), transceiver used, and intended device usage.

  - Standard Configuration Property Type (SCPT): Pronounced "skip-it." A standard format type maintained by LonMark for configuration properties.

  - Standard Network Variable Type (SNVT): Pronounced "snivet." A standard format type maintained by LonMark used to define data information transmitted and received by individual nodes. "SNVT" is used in two ways. It is an acronym for "Standard Network Variable Type" and is often used to indicate a network variable itself (i.e., it can mean "a network variable of a standard network variable type").

  - Subnet: Consists of a logical grouping of up to 127 nodes, where logical grouping is defined by node addressing. Each subnet is assigned a number, which is unique within a Domain. See "Node Address."

  - TP/FT-10: Free Topology Twisted Pair network defined by CTA-709.3 and is most common media type for a CTA-709.1-D control network.

  - TP/XF-1250: High-speed, 1.25 Mbps, twisted-pair, doubly terminated bus network defined by "LonMark Interoperability Guidelines" and typically used only to connect multiple TP/FT-10 networks.

  - User-Defined Configuration Property Type (UCPT): Pronounced "u-keep-it." A Configuration Property format type that is defined by device manufacturer.

  - User-Defined Network Variable Type (UNVT): Network variable format defined by device manufacturer. UNVTs create non-standard communications that other vendors' devices may not correctly interpret and may negatively impact system operation. UNVTs are not allowed.

- Low Voltage: As defined in NFPA 70 for circuits and equipment operating at less than 50 V or for remote-control, signaling power-limited circuits.

- Mobile Device: A data-enabled phone or tablet computer capable of connecting to a cellular data network and running a native control application or accessing a web interface.

- Modbus TCP/IP: An open protocol for exchange of process data.

- MS/TP: Master-slave/token-passing, ISO/IEC/IEEE 8802-3. Datalink protocol LAN option that uses twisted-pair wire for low-speed communication.

  - Note: this terminology should be avoided in favor of Primary/Secondary or Source/Replica when used in specifications, drawing packages or in verbal communication. The colloquial terminology is provided above only due to the lack of a ratified replacement terminology and to highlight the requirement to limit its use.

- Network Controller: Digital controller, which supports a family of programmable application controllers and application-specific controllers, that communicates on peer-to-peer network for transmission of global data.

- Network Repeater: Device that receives data packet from one network and rebroadcasts it to another network. No routing information is added to protocol.

- Operational Technology / OT Network / Industrial Control ICS

  - A physical or logical connection of devices for the purpose of connecting, monitoring, managing, and securing an organization's industrial operations

- Patch Panel: A system of terminal blocks, patch cords, and backboards that facilitate administration of cross-connecting cables.

- Peer to Peer: Networking architecture that treats all network stations as equal partners.

- Point

  - Terminology for a control operation in a system which could be sensing or controlling (collecting or modifying).

  - A point is a subset of data to be captured, modified and shared by a system and which may be made accessible to other integrated systems to be read from or written to.

- Protocol Implementation Conformance Statement (PICS):  All devices conforming to the BACnet protocol must have a Protocol Implementation Conformance Statement (PICS) that identifies all of the portions of BACnet that are implemented.

- QNX: Unix-like real-time operating system primarily used with embedded systems.  As a microkernel-based OS, QNX is based on the idea of running most of the operating system kernel in the form of a number of small tasks, named Resource Managers.

- Raceway: Any pipe, duct, extended enclosure, or conduit (as specified for a particular system) which is used to contain wires and which is of such nature as to require that the wires be installed by a pulling in procedure. Where the word “conduit” is used without specific reference to type, it must be understood to mean “raceway”.

- Router: Device connecting two or more networks at network layer.

- Server: Computer used to maintain system configuration, historical and programming database.

- User Datagram Protocol (UDP): This protocol assumes that the IP is used as the underlying protocol.

- Zigbee: IEEE 802.15.4-based specification for a suite of high-level communication protocols used to create personal area networks with small, low-power digital radios. Zigbee is a low-power, low data rate, and close proximity (i.e., personal area) wireless ad hoc network.

- Z-Wave: A wireless communications protocol that forms a mesh network using low-energy radio waves to communicate from appliance to appliance.

# Abbreviations and Acronyms

          - ANSI 		American National Standards Institute

          - AFF 		Above Finished Floor

          - AHJ			Authority Having Jurisdiction

          - ARC			Aluminum Rigid Conduit

          - AWG		American Wire Gauge

          - AV 			Audio / Visual, audiovisual, audio visual

          - Avixa		Audiovisual and Integrated Experience Association, formerly InfoComm

          - BAS 		Building Automation Systems

          - BTU 		British thermal Unit

          - COV		Changes of value.

          - °F 			degrees Fahrenheit

          - ft 			feet

          - EMT			Electrical Metallic Tubing

          - FT 			Fiber Transceiver

          - GbE 		Gigabit Ethernet

          - GRC		Galvanized Rigid Conduit

          - HLC			Heavy load conditions.

          - HTML 		HyperText Markup Language

          - HUIT		Harvard University Information Technology

          - HUPD		Harvard University Police Department

          - HU			Harvard University

          - Hz 			Frequency in Hertz (k = kilo, M = Mega, G = Giga)

          - ID			Inside Diameter

          - in 			inch

          - lbs 			pounds

          - IMC			Intermediate Metallic Conduit

          - IP 			Internet Protocol

          - ISO			International Organization for Standardization

          - LAN			Local Area Network

          - LNS			LonWorks Network Services.

          - MAC		Media Access Control (Address)

          - Mbps 		Megabits per second

          - MTBF		Mean time between failures.

          - NEC			National Electrical Code

          - NEMA		National Electrical Manufacturing Association

          - OD 			Outside Diameter

          - PICS		Protocol Implementation Conformance Statement

          - PM			Project Manager

          - PoE			Power-over-Ethernet protocol

          - POT			Portable operator's terminal.

          - PVC 		Polyvinyl Chloride

          - RAM		Random access memory.

          - RF			Radio frequency.

          - RNC		Rigid non-metallic conduit

          - RU 			Rack Unit

          - SNMP 		Simple Network Management Protocol

          - TCP 		Transmission Control Protocol

          - TCP/IP		Transport control protocol/Internet protocol.

          - TIA			Telecommunications Industry Association

          - TGB			Telecommunications grounding busbar

          - TIA 			Telecommunications Industry Association

          - TMGB		Telecommunications main grounding busbar

          - TR			Telecommunications Room

          - UPS 		Uninterruptible Power Supply

          - USB			Universal Serial Bus.

          - UL 			Underwriters Laboratories

          - VAV			Variable air volume.

          - VLAN 		Virtual Local Area Network

          - VoIP 		Voice over Internet Protocol

          - VPN 		Virtual Private Network

          - WAN 		Wide Area Network

          - WLED		White light emitting diode.

          - WLAN 		Wireless Local Area Network

# Supporting Resources

HUIT maintains a list of supporting resources for this guideline. Links to publicly available resources have been provided below. Where resources are stored in a HUIT controlled repository or where regular updates preclude providing a static link, request access or current versions via email to: othelp@harvard.edu

- Harvard University Building Integration Foundational Technology Decision Points

  - A list of potential supported integrations which may benefit a project. This list is formatted as a series of project programming decision points with the integration coordination impacts listed.

  - It is recommended that this list of foundational technology decision points be completed by the project business owners and design team prior to specification of integrations.

  - ShareFile Link: Request a current link from HUIT at the start of the project

- Harvard University Operational Technology preferred vendors/manufacturers

  - ShareFile Link: Request a current link from HUIT at the start of the project

- Harvard University “IT Operational Technology Rules of the Road for Integrators and Installers”

  - Guideline for transitioning a networked system or device from construction to operations

  - Latest version must be downloaded from HU ShareFile location. If the link to the ShareFile is not functional – it must be the responsibility of the Security Contractor to obtain latest version of “HUIT OT Rules of The Road for Integrator and Installers” from HUIT project manager.

  - ShareFile Link: Link

- Harvard University Cyber Hardening Guidelines

  - A list of minimum required areas of network hardening to be addressed by the OT vendor prior to deployment of a device

  - Information capture in the Requirements for Access to and Protection of the Harvard Network Contract Rider

- Harvard University Campus Services Building Management Systems Security Policy and Guideline

  - Policy for safeguarding the integrity of computing systems at Campus Services and Harvard University that is to be reviewed and executed by all vendors and any parties responsible for the configuration or deployment of hardware installed in Harvard University facilities

  - Note: This policy is only required for Harvard Building Management Systems maintained by Campus Systems. The Rider covers all hardware connected to Harvard networks.

  - ShareFile Link: Request a current link from HUIT at the start of the project

- Harvard University Operational Technology Device Connection Request Form

  - Request form for devices which have not previously been deployed on the HU OT network or for devices which have undergone significant updates and require new access levels/capabilities for operation.

  - ShareFile Link: Request a current link from HUIT at the start of the project

- Harvard University Network Access Rider

  - Service provider rider required of all service providers if directly plugging a computer or other device into a network jack at Harvard, being provided Harvard credentials to access non-guest networks or provide/install/support any computer devices on a HUIT network.

  - ShareFile Link: Request a current link from HUIT at the start of the project

- Harvard University Requirements for Access to and Protection of the Harvard Network.

  - ShareFile Link: Request a current link from HUIT at the start of the project

- Harvard Building Information Modelling Standards

  - ShareFile Link: Request a current link from HUIT at the start of the project

- Harvard Graphic and Naming Standards

  - ShareFile Link: Request a current link from HUIT at the start of the project

- Harvard University OT network/device testing plan checklist

  - ShareFile Link: Request a current link from HUIT at the start of the project

# Preferred Vendors

- Vendors/ Integrators of Industrial Control Systems and Operational Systems at Harvard University

  - Refer to the Appendix A – Harvard University Operational Technology preferred vendors/manufacturers for a list of preferred vendors for the ICS/OT systems

    - The list of preferred vendors must be annually updated based upon vendor performance.

    - The listed preferred vendors have been identified as being able to be successfully deployed and integrated into Harvard’s facilities and networks while retaining the core functionality of the systems and meeting the operational requirements of the business unit/owner they serve.

    - It should be understood that any prior use of the preferred vendors systems or completion of past network security assessments completed does not excuse the vendor from following HUIT guidelines and rules of the road.

    - Where a substitution from the preferred vendor list is required to meet a new operational requirement, the party requesting the substitution (Project Architect, Project Engineer, Integrator, Vendor or HU Business Owner) must complete the Harvard University OT Network Access Request Form and receive approval prior to specification or deployment

    - Where a new product line or major hardware/software update by a preferred vendor/manufacturer is selected for a Harvard University facility, the “OT Network Access Request Form” must be modified and resubmitted for approval prior to specification or deployment

# Selecting the Appropriate Specifying Division

- To avoid gaps in installation, configuration and ongoing service responsibilities between the various project manufacturers/vendors, integrators, and General Contractor; all integration responsibilities must be documented as part of the CSI MasterFormat Division in which the controlling hardware is provided.

- In most cases this will mean that a separate Division 25 specification section to support the specified integrations may not be required. See the integration example below.

  - Example: Audiovisual systems processors integrated with Architectural Lighting processors to allow recall of lighting presets from AV touch panels.

    - Lighting processors are specified under Division 26

      - Lighting integrator responsibilities must be specified as part of this division

    - Audiovisual processors are specified under Division 27

      - Audiovisual integrator responsibilities must be specified as part of this division

    - Pathways (conduit, trunking, etc.) are specified under Division 26 or 27

    - OT network data lines are documented as part of the Division 27 structured cabling

    - OT network hardware to connect the lighting and AV processors is configurated and furnished by HUIT and physically installed by Division 27.

    - As no other third-party systems or master controllers are required to complete this integration, a separate Division 25 specification section to support this integration is not required.

- When a dedicated Division 25 specification section is required

  - To avoid creation of an orphaned specification section, a Division 25, Integrated Automation, specification must be provided only when a dedicated Integration Automation integrator contract, separate from the Division 23 BAS/BMS contract or a Harvard University Furnished OT network contract, is to be executed.

# Specification Level of Detail

- Integration specifications are often written with line-item technology protocol and expectations on manufacturers technologies to operate in a way that mirrors the specifications.

- It is more often the case that integrations are utilizing manufacturer’s existing products and integration capabilities or new products which were not anticipated when the specification was written or who’s use was not influenced by the specification itself but because the capability was a default capability of the product already.

- Because of this, it is recommended that specifications should follow the format of:

  - Define intended experience and impact to the building and user

    - Define integrations supporting those experiences

    - Define integration responsibilities

    - Define key technologies which are required to support the ability for the disparate platforms to integrate

    - Define the parameters which are required to support the sharing of data and effect the integration

    - Define the security and operational parameters of the integration

- Specifiers are cautioned to avoid defining technologies to be used or communication protocols required when they are already a part of approved manufacturer/vendor’s base product suite as this adds information which is not natively controllable by the specifier and could lock the manufacturer/vendor into providing a deprecated version of the product to meet an out of date specification requirement.

- Specifications should list communication protocol governing bodies and require that the current and stable versions of each protocol be deployed and to prohibit the use of deprecated or unstable protocol versions.

- The exception to reducing the specificity of protocol information in the specification would be when a new implementation of a protocol is required or where listing a specific technology is necessary to provide an experience not otherwise possible without its use.

# Specifier’s Responsibilities

- The specifying engineer is responsible for the following tasks:

  - Identifying and documenting integration requirements and system components

  - Documenting the Business Owners impacted by the selected integration and identifying any unique operational or business cases that may impact the requirements or hardware selected for the integration

    - Identification of the appropriate business owners and coordinating review sessions with the impacted parties must be the responsibility of HU project management.

  - Validating with HUIT that the required integration can be supported by the HU OT network

    - Where a new integration or preferred manufacturer not previously supported by the HUIT OT network is requested, the specifying engineer must complete the initial portions of the “Operational Technology Network Access Request Form” and furnish to HUIT for approval prior to specifying

  - Documenting OT network requirements to support the specified integration and providing to HUIT.

    - HUIT must select the appropriate network hardware to support the OT network requirements, configure the network hardware and furnish to the project for installation under the Division 27 scope of work.

    - Identify if remote access is needed during deployment or as part of the final integration for operational support

    - Coordinate OT network requirements with othelp@harvard.edu

  - Coordinating supporting systems requirements (electrical, mechanical, architectural, etc.) with associated trade designers and engineers.  The specifying engineer must coordinate integration requirements with the equipment specified in the other divisions that will communicate with the integrated system.  Appropriate references must be coordinated and listed between the other divisions within each appropriate specification section.  For example, if a walk-in cold room, purified water system skid or air handling unit is specified to include integral controls within the associated Division 13, 22 and 23 sections, references must be included within the Division 13, 22 and 23 sections as well as the Division 25 section to define intercommunication requirements.  Note, all final testing requirements must remain under the Division 25 contractor responsibilities.

  - Evaluating the work of the selected integrator/s

- The specifying engineer is responsible for the following deliverables prior to contracting of integration services:

  - Drawing package documenting the integration hardware and supporting infrastructure to a Building Information Modelling (BIM) Level of Development 300 (LOD 300) as defined by the American Institute of Architects (AIA).

    - Where a 2D documentation platform is used (AutoCAD or similar) the LOD format may be maintained.

    - Drawings must include:

      - Network architecture diagram(s).  The diagram(s) must include tie in points for all integrated systems.  If the network diagrams of the systems to be integrated are documented within the drawing sets of the other disciplines, then appropriate references must be included on all appropriate Division drawings, including Division 25 network architecture diagram.

      - Control diagrams for each system documenting main equipment such as chilled water and heating hot water systems, air handling units, fans emergency generators.  For systems/equipment that are complete matches, a typical diagram may be developed provided that all relevant equipment numbers are listed.   Diagrams must indicate each control device and corresponding setpoint, including alarms.

      - Control diagrams for each typical room/space configuration.  Each unique room configuration must be documented.

      - Control device installation details. (may also be provided as part of the specifications)

      - A final list of all drawings required for the project must be reviewed with the project manager prior to issuance of the specifications for bid.

  - Coordinated CSI Masterformat Specification Sections detailing the hardware and software requirements as well as the selected integrations

    - Control and monitoring devices.  Include relevant requirements such as ambient condition limitations, desired accuracy, response times, etc.

    - System communication hardware and software requirements.  Include requirements for new workstations if relevant for a given project.  For projects concerning modifications to existing systems, include necessary hardware and software requirements to allow for communication and integration between the new and existing components.

    - Integration Matrix

      - Description of the integrations required

      - Identification of the Divisions required for each integration

      - Identification of the data types to be managed for each integration

      - Read or Write status for each data type

      - A single source of truth (SSOT) for each data type (see SSOT section)

      - Description of the user controls required

      - Description of the failure mode for each integration

    - Integration Sequence of Operations.  Sequences must include requirements for each MEP system and interaction requirements between them.

      - Sequences of operations to be provided in specification narrative form rather than included with each system control diagram

    - Specification sections must include a points list identifying:

      - Point description (system serving, details)

      - Format (analog, digital, input, output, etc.)

      - Interface Type

      - Controlling device details

      - BACnet writable (yes, no)

      - Alarm requirement

      - Trending requirement

      - Visible on user interface requirement

      - Point Responsibilities (Furnish, Install, Commission)

    - Any specification sections requiring OT network integration must reference this document as an appendix with a link to the live version of these guidelines

    - Scope of Responsibilities (see SoR Matrix section)

    - Submittal Requirements (see Submittals section)

    - Commissioning and Demonstration requirements (see Commissioning & Demonstration section)

    - Ownership of custom software & programming requirements (see custom software & programming section)

    - Warrantee and service contract requirements (see Warrantee and service contract section)

- Where demolition or decommissioning of part of the entirety of an OT system or associated components is required as part of the scope of work the Specifying Engineer must define:

  - Responsibilities for protecting in place, protecting and storing remotely, decommissioning and disposing, decommissioning and turning over to HU for future use or preparing for reuse as part of the associated scope of work must be defined as part of the specification.

  - Where temporary offsite storage at a contractor’s facility is required, define requirements to secure and audit the equipment

  - Where equipment is to be reused, define responsibilities to test prior to reinstallation, upgrade to current stable firmware and to identify costs associated with replacement of damaged or unsupported devices identified as part of the testing process.

# System Integrator’s Responsibilities

- The systems integrator is responsible for the following tasks:

  - Validation of the integration requirements and the ability for the specified hardware to perform the required integrations

  - Final systems engineering and hardware design

  - Systems Submittals (see Submittals section)

  - Programming and configuration of the integration software

  - Installation of all hardware and software

  - Coordinating with all associated trades required for the integration

  - Systems commissioning (see Commissioning & Demonstration section)

  - System notification, alert and alarm settings

    - The definition of what constitutes a critical alarm should be defined by the Harvard / Construction PM. The PM shall engage and inform the campus services operations team as part of this process

  - System warrantee and service contract (see Warrantee and service contract section)

- Where demolition or decommissioning of part of the entirety of an OT system or associated components is required as part of the scope of work:

  - Integrator will follow the specification requirements for demolition, protection, storing and reuse of the OT hardware.

  - ICS and OT devices marked for reuse will be reset or erased to its default settings and verified with the Business Owner and OT contact.

  - ICS and OT devices marked for demolition will use Harvard University shredding/disposal service.

# Scope of Responsibilities Matrix

- All projects require that a scope of responsibilities matrix be provided as part of the design deliverables. It is recommended that this matrix be initially submitted during the schematic design phase and reviewed at the completion of Design Development and Construction Documents. This matrix should be referenced in the systems integration RFP and/or individual specification sections detailing systems integrations.

- Example:

| System Item | Package/ Budget | Furnish | Install | Configure | Integrate | Notes |
| --- | --- | --- | --- | --- | --- | --- |
| Occupancy Platform |  |  |  |  |  |  |
| Low voltage pathways & pull strings (conduit, backboxes, etc.) | Electrical | Electrical Contractor |  |  |  | Refer to technology packages for scope |
| Occupancy Sensor - Lighting | Electrical | Electrical Contractor |  | Lighting programmer | Space Management | Refer to architectural lighting plans for scope |
| Space Management IAQ Sensor | Owner | Owner | Structured Cabling | Space Management | Space Management | OFE as part of space management OPEX contract. |
| Space Management Platform | Owner | Owner | Owner | Space Management | Space Management | OFE as part of space management OPEX contract. |

# Integrator Submittals

- The minimum integration submittal requirements included in any specification sections defining systems integrations must meet the requirements listed within this section.

- If multiple submissions are required to execute work within project construction schedule, first submit a coordinated schedule clearly defining intent of multiple submissions. Include a proposed date of each submission with a detailed description of submittal content to be included in each submission.

- Contractor must receive approval from the Owner or Design Professional of a submittal before procuring equipment or performing services related to the submittal. (Critical point!)

- All submittals must be provided in electronic format.

  - Drawings must be developed in accordance with University standards.

  - Provide one full size paper submittal if requested by Owner.

  - Confirmation of the submittal schedule and submission format must be obtained by Owner prior to creating individual submissions.

- Revised submittals must include clouding or other method to indicate revisions since the prior submission.

- Project Status Report

  - A project status report must be sent to the Owner and Design Professional weekly starting within two weeks of award. The project status report must be used as the basis for Contractor coordination meetings and must include:

    - Team member contact information

    - Project overall schedule

      - Highlight changes to the schedule since last issuance

      - Identify critical schedule items

      - Identify opportunities to improve on the current schedule

    - Action items from prior coordination meeting and status of each item

    - Installation schedule and status for each unique space or system in the project.

    - Outstanding Owner coordination items.

    - Outstanding Design Professional coordination items.

    - Change Order Status

    - Submittal Approval Status

- Within 45 days of award, submit an installation schedule including major milestone dates for construction phasing based on overall project construction schedule (along with separate phases where applicable), system and device configuration, testing and training. Include the following milestones:

  - Separate milestones for each submittal.

  - Required date for receipt of all OFE equipment, including network hardware, per project phase or equipment type.

  - Contractor’s project manager onsite.

  - Cable pulls start and complete

  - Hardware rough-in start and complete

  - HU OT network required go-live date

  - Equipment installations start and complete

  - Systems configuration and testing start and complete

  - Systems ready for checkout and punch list

  - Owner training sessions

    - System operators

    - Business Owner administrators

    - HUIT support team

  - Formal systems turnover date – Operational start date

  - As-built submission

- Within 90 days of award submit a system infrastructure review memo confirming infrastructure shown on the Architectural, Civil, Telecom, Mechanical, Plumbing, Fire Protection, and Electrical design packages or any other trade packages necessary to support this scope of work meets the integration equipment installation requirements. Where necessary, identify specific adjustments necessary to support the equipment installed under this scope of work.

  - Verify conduit sizing and pathways

  - Verify architectural coordination elements

  - Verify data drops to support integration network connectivity

    - Provide markups of the telecommunications drawing set indicating where OT devices will use infrastructure shown in the telecommunications set and identify any locations where additional infrastructure is required to support OT hardware.

  - Verify power receptacles and multi-discipline shared services device requirements (in-wall boxes, floor boxes, poke-thrus.

  - Verify integration hardware cooling/exhaust requirements

- Submit proposed product data sheets for each control and monitoring component, panels/enclosure, as well as network communication devices.  Product data must include workstation components if applicable to the given project.  The Contractor must submit catalogue cut-sheets that include manufacturer, trade name, and complete model number for each product specified or selected for use in the project.  Product data sheets must include identifiers to define application of each.  Reliance on keying product data by model numbers listed within the system diagrams is not acceptable.

  - All cut sheets must be obtained from the manufacturer at the time of submission to make certain the current product specifications and characteristics have been provided.

  - Model number must be highlighted to indicate exact selection per system type.

  - Product data sheets must be organized with separate folders per system type with a master equipment list broken into three sections:

    - System types and quantities of systems

    - Equipment and equipment quantities per system type

    - Master project equipment list and quantities

  - Schedule and design calculations for selection of all flow sensors, control dampers, control valves and actuators.  All relevant data must be listed such as flow, velocity and pressure drop.

  - Confirm manufacturer master quote numbers and the accuracy of the master quotes against the specified equipment.

- Submit a list of all required wireless frequencies to HUIT for approval

- Submit shop drawings detailing proposed system architecture and interconnectivity.

  - All shop drawings sheets must be sized to match the University’s drawing format.

  - Symbols, abbreviations and notes, including wiring legends.

  - Network architecture diagram(s).

    - Network diagrams must be specific to each project and detail all components and systems connected, including wired and wireless devices.  Typical diagrams are not acceptable.

    - For each network, indicate communication protocol, speed and physical means of interconnecting network devices, such as copper cable type, or optical fiber cable type. Indicate raceway type and size for each.

    - For each network, indicate each point of connection to field power with requirements (volts/phase//hertz/amperes/connection type) listed for each.

  - Control diagram for each system and equipment.  For systems/equipment that are complete matches, typical diagrams are not acceptable since point identifier numbers are unique for each system.    Diagrams must indicate each control device and corresponding setpoint, including alarms.

  - Control diagrams for each typical room/space configuration.  Each unique room configuration must be documented.  Each typical diagram must list applicable room/space name and number.  In addition, all relevant terminal devices such as VAV boxes or fan power boxes must be listed by their corresponding tag number.

  - Control and monitoring device installation requirements must be indicated on the relevant control diagrams.

  - System diagrams must include cable labels and corresponding cable schedule indicating wiring interconnections between all devices and Owner’s network.

  - Points lists must include:

    - Point description (system serving, details)

    - Format (analog, digital, input, output, etc.)

    - Interface Type

    - Controlling device details

    - BACnet writable (yes, no)

    - Alarm requirement

    - Trending requirement

    - Visible on user interface requirement

    - Point Responsibilities (Furnish, Install, Commission)

  - Integration Sequence of Operations.  Sequences must include requirements for each MEP system and interaction requirements between them.  Sequences must be included for each system and equipment, as well as each typical room configuration.  Sequences must not be exact copies of the engineer’s performance-based sequences.  The submitted sequences must include specific requirements for each system and component to detail a complete sequence.

    - Sequence of operations must be documented in specification narrative form rather than included with each system control diagram

  - Shop drawings must include the following drawing information:

    - Scaled floor plans indicating the area of work and room types.

    - Enlarged plans indicating equipment locations, mounting requirements, clearances, infrastructure requirements, and cable routing.  Plan drawings must include locations of main network equipment and workstations, including panels, network switches, etc.  Indicate each network port connection points for an operator workstation or other type of operator interface with unique identification for each.

    - Device details indicating mounting requirements for each unique equipment type in the project.

      - All overhead equipment details must identify the safe working load and manufacturer provided safety hardware. Where a custom mounting detail is required using fabricated components or components provided by multiple manufacturers a structural detail, reviewed, and stamped by a Structural Engineer licensed in the project state, must be provided.

      - Copies of manufacturer cut sheet details must not be considered sufficiently coordinated.

    - Rack elevations and mounting details with clearances and infrastructure requirements

    - Wiring termination details.

      - Include cable labelling standards and materials

    - Control panel drawings indicating the following:

      - Panel dimensions and materials

      - Interior subpanel layout, drawn to scale and showing all internal components, cabling and wiring raceways, nameplates, and allocated spare space.

      - Connector types.

      - Labels

      - Front, rear, and side elevations and nameplate legend.

      - Unique drawing for each panel.

    - Technical Furniture details indicating the location, required openings and cable management of all equipment in furniture and millwork regardless of the scope of work the furniture is provided under.

- Description and technical data of all software provided and cross-referenced to products in which software will be installed.

  - Vendor(s) must include a bill of materials on the frameworks/drivers their software is based upon.  Appropriate Harvard University staff will review submittal to understand the risks associated with the platforms.

  - Vendor(s) submit a licensed evaluation copy of their product for evaluation.

  - Include latest software and hardware release notes and white papers.

  - Include a current disaster recovery plan for any cloud or managed applications

- Once previous submittals have been reviewed and approved submit a graphics submittal.   The graphics submittal must include the following:

  - Itemized list of color graphic displays to be provided.

  - For each display screen to be provided, a true color copy showing layout of pictures, graphics, and data displayed.

  - Intended operator access between related hierarchical display screens.

  - Refer to HU graphics and naming standards

    - At this time it is necessary to request a copy of the current naming standards from the project manager.

- Control Systems User Interface Submittals

  - Where custom user interfaces are required to meet the integration requirements, and the use of custom interfaces has been approved by HU, Vendor must obtain Owner or Design Professional approval of all integration user interface submittals required prior to installation. Failure to secure approval must not be grounds for project schedule delay or Contractor change order.

  - Submit button panel layouts with labelling/engraving and sequence of operations.

  - Submit an initial and up to two revised set of user interface submittals.

    - Contractor must lead a user interface review session with Owner and Design Professional prior to start of user interface design. Contractor must provide up to three design samples in advance of the user interface session for Owner and Design Professional review.

      - HU will coordinate attendance at this session by a HU technical resource who will support the application for the Business Owner.

    - User interface layouts must follow any ANSI or established industry trade organization best practice.

    - User interfaces must include the following basic features:

      - Control of all equipment addressable parameters required during the specified use cases.

      - Standard controls formatted to match industry standard applications (knobs, sliders, buttons, interactive menus, etc.)

      - A password protected advanced section allowing for control of individual device parameters (power, channel level controls, input selection, etc.)

      - Utilize stock manufacturer pages and capabilities where possible. Custom scripting must be avoided unless where required as part of this specification.

- Network Coordination Submittal

  - Submit a detailed list of all network enabled devices detailing:

    - Device name/model and manufacturer

    - Intended installation location

    - Type of network connection (wired, wireless, other protocol)

    - MAC address

    - IP Address (for Owner to complete)

    - Subnet (for Owner to complete)

    - Wired and Wireless VLANs

    - DHCP requirement

    - Unique network requirements including firewall exceptions, port forwarding and Qos

  - Lead an integration network coordination session with the Owner and Design Professional to confirm overall project integration network requirements and set a schedule for completion and return of the Network Coordination Submittal by the Owner.

  - Along with updating the above based on final as-built conditions, revise the submittal as part of the final as-built drawings to indicate location of the devices, field data jack number, IDF/TR rack patchbay number and installed firmware version.

- Owner Training Plan

  - Identify specific systems to be trained on and training durations.

  - Identify required project stakeholders.

  - Identify training status and provide training sign-off sheets.

  - Provide training materials and user one-page operations sheets for each system types.

- Operations and Maintenance Manuals:

  - This Section requires complete documentation of systems integrations for the purpose of system operation and maintenance during and after the Warranty period. It is intended that the operation and maintenance manuals be exhaustive in the coverage of the system to the extent that they may be used as the sole guide to the troubleshooting, identification, and repair of defective parts. All documentation, as described here-in must be submitted to the Owner for approval sixty (60) days prior to final submission.

  - Scope:  These manuals must include basic wiring diagrams, schematics, and functional details such that any component, wire, or piece of equipment in the system may be easily identified by going to the actual equipment and making reference to this manual. It is required that everything in the system be neatly labeled and easily identifiable. Every terminal, wire, component, or piece of equipment, and other such items must have a number or letter designation. All of these identification characteristics must be included in the maintenance and operation manuals.

  - The maintenance manual requirement of this Section is in addition to Shop Drawing requirements.  Maintenance manuals and Drawing sets must be compiled after system fabrication and testing and must incorporate any changes made after Shop Drawing submittal. The maintenance manuals and drawing books must be permanently bound in hard plastic covers.

  - Maintenance Manuals, Manufacturer's Literature: Provide manufacturer's standard literature, covering all equipment included in the system. The maintenance manuals must contain specifications, adjustment procedures, circuit schematics, component location diagrams, and replacement parts identification. All references to equipment not supplied on this Project must be crossed out.

  - System Administrator Documentation: This documentation must provide complete information on the configuration, business rules, operation, maintenance, and trouble-shooting of the system.

- Testing Plan

  - Submit a systems testing and verification plan for approval by Owner and Design Professional.

    - The testing plan must be based on a HU provided testing checklist.

  - The approved Testing Plan must be completed and provided to the Owner and Design Professional prior to commencement of Owner testing and punch list efforts.

  - The testing plan must include a current installation schedule and must be coordinated to be completed prior to commissioning of any systems tied to the OT network or specific integrations under test.

- As-built Documentation

  - Submit an updated version of all submittals revised to match installed conditions.

  - Submit the native version of all drawing, control programming, digital signal processing and other systems configuration files.

  - A set of project programming files and other configuration files should be sha-256 hashed when finalized and backed up to validate no changes have been made to the data set once the system has been signed off and turned over to HU.

    - The config files should be provided to HU at the end of each project via OThelp@harvard.edu

- Warranty

  - Within 30 business days of award, provide a summary of the systems warrantee including all optional services for final Owner confirmation.

  - At time of as-built documentation submission provide two physical copies of the hardware and software warranty certifying that the final as-built installation is fully warranted by the manufacturer.

# ISC/OT Network Labelling and Asset Management

- Device Labelling

  - All ICS/OT Systems and devices will be labeled to according to Harvard University Policy.

  - All labels will need reviewed by the Business owner of OT/ Labeling will not include IP address or account information which is stated in the Harvard University Rider: Requirements for Access to and Protection of the Harvard Network.

- Asset Tracking / Management

  - Asset data is to be provided to HU and must follow the individual asset management tracking requirements (tags, offsite cataloging, replacement periods, etc.) of the program/school the assets are dedicated to.

  - Coordinate asset data format and requirements with HU prior to issuing.

# System Commissioning & Demonstration Requirements

- The minimum system commissioning and demonstration requirements included in any specification sections defining systems integrations must be as follows

- Temporary passwords must be assigned during construction/installation to allow contractor to complete their scope.  Temporary passwords must be removed once Harvard University accepts the given project.

- Project Testing: The integrations identified in this specification must not be considered complete until On-Site Testing is completed. The purpose is to test the complete system and demonstrate that all specified features and performance criteria are met. All requirements of the specification must be tested.

- Contractor must document all commissioning tests performed and submit a completed testing plan prior to final Owner and Design Professional testing.

- Design Professional may elect to request retesting of individual integration features or demonstration of the integration at multiple locations throughout the project site until satisfied those systems are properly installed and configured.

- For any system or equipment integration commissioning parameters not covered in this specification which are required for normal system operation, Contractor must provide a proposed test plan/procedure for each testing phase for review by the Owner or Design Professional. The test plan for each phase of testing must detail the objectives of all tests. The tests must clearly demonstrate that the system and its components fully comply with the requirements specified herein. The submission of Test Plans must adhere to the following:

  - A draft test plan must be presented to the Owner at least forty-five (45) days prior to the scheduled start of each test.

  - A workshop for reviewing comments must be conducted with the Owner at least thirty (30) days prior to the scheduled start of each test.

  - A final test plan must be submitted to the Owner at least fourteen (14) days prior to the scheduled start of each test.

  - Test plans must contain at a minimum:

    - Functional procedures including use of any test or sample data.

    - Test equipment is to be identified by manufacturer and model.

    - Interconnection of test equipment and steps of operation must be defined.

    - Expected results required to comply with specifications.

    - Testing matrix referencing Specification requirements with specific test procedures.

    - Record of test results with witness initials or signature and date performed.

    - Pass or fail evaluation with comments.

- The test procedures must provide conformity to all Specification requirements. Satisfactory completion of the test procedure is necessary as a condition of system acceptance.

- The test procedures must demonstrate integration failure modes and document the behaviors of the individual sub-systems for individual and system-wide integration failures.

  - Demonstrate integration failures due to power loss, network outage, component failures and operator misuse.

  - Upon request, any integrations which are tied to life-safety systems must include a separate testing session with HU facilities, HUIT, the Business Owner and the local AHJ to demonstrate compliance with all life safety code requirements.

- All Test plans must be reviewed by the Owner or Design Professional. To successfully complete a test, the test document must be signed and dated by both the Contractor and the Owner.

- The Owner or Design Professional will review, witness and validate the execution of all formal test procedures prepared by the Contractor and deliverable under the contract to assure the tests cover all requirements and that there is a conformity between the conducted test, the test results and Specification requirements.

- Documentation verification both interconnects and operationally, must be part of the test. Where documentation is not in accordance with the installed system interconnect and operating procedures, the system must not be considered accepted until the system and documentation correlate.

- The Contractor must provide the Owner or Owner representative the opportunity to participate in any or all of tests.

- Test Reports: The Contractor must prepare, for each test, a test report document that must certify successful completion of that test. Submit to the Owner's representative for review and acceptance within seven (7) days following each test. The test report must contain, at a minimum:

  - System power measurement results and settings

  - Commentary on test results

  - A listing and discussion of all discrepancies between expected and actual results and of all failures encountered during the test and their resolution.

  - Complete copy of test procedures and test data sheets with annotations showing dates, times, initials, and any other annotations entered during execution of the test.

  - Signatures of persons who performed and witnessed the test

  - Test Resolution: Any discrepancies or problems discovered during these tests must be corrected by the Contractor at no cost to the Owner. The problems identified must be corrected and the percentage of the entire system re-tested determined by the Owner before any subsequent testing is performed.

- A backup of all ICS/OT systems will be done after commissioning and reviewed by the Business owner.

- Configuration changes which were made during commissioning will be removed if no longer needed

- All ICS /OT systems will be scanned for vulnerabilities before IP addressable device is added to the Harvard Network and after commissioning.

# Warrantee and Service Contract

- All ICS/OT Systems must have a formal support contract to perform quarterly patching and maintenance.  The contract will be provided to the business owner of the system on a yearly basis

- The minimum contractual warrantee included in any specification sections defining systems integrations must be:

  - The system warranty must commence on the date of Substantial Completion unless otherwise provided for in the Contract.

  - The system warranty must be for an initial period of one year

  - Hardware Warranty:

    - Contractor must warrant that all components meet or exceed the specifications provided in the product data submittal.

    - The Contractor must warrant that the proposed merchandise will conform to its description and any applicable specifications and must be of good quality for the known purpose for which it is intended.

    - The warranty must cover material and labor for the replacement or repair of defective products.

    - Regardless of manufacturer warranties expiring before the full system warranty period, Contractor must be responsible for extending any manufacturer warranties for the full length of the system warranty.

  - Software Warranty:

    - The warranty must allow for replacement or repair at the discretion of the Owner. All software necessary to compile, modify, and maintain software developed for this specification must be included in this warranty.

    - The warranties must include the price of all software upgrades during the warranty period. If a new version of the system software becomes available during the warranty period, it must be upgraded as part of the warranty.

- The minimum contractual service contract included in any specification sections defining systems integrations must be:

  - During the warranty period provide 24-hour, 7 days a week live monitoring of the system from the Contractor’s operations center. Provide customer service for subscriber issues Monday – Friday, 9am – 5pm local time. Provide quarterly system inspections, checks and updates during the warranty and maintenance period.

  - Personnel: Service personnel must be certified in the maintenance and repair of similar types of equipment and qualified to accomplish work promptly and satisfactorily. The Owner or Owner’s Designated Representative must be advised in writing of the name of the designated service representative, and of any change in personnel.

  - Schedule of Work: The Contractor must perform quarterly inspections of the installed system. Inspections must be in accordance with manufacturer and Contractor recommendations. The adjustment and repair of the system must include visual checks of installed equipment and inspection of system health logs and software.

  - Where required for the ongoing stability and security of the integrations, recommended software updates must be applied on the system at these pre-defined quarterly periods.

    - The safe deployment of software updates, including coordinating with any third-party vendors or manufacturers to make certain that the updates will be compatible with the integrations provided, requires that all updates are pre-planned and validated prior to applying.

    - At no point will an update be allowed to reverse or circumvent any security controls put in place during system installation, commissioning or turn-over.

    - A software update plan identifying the targeted system, potentially impacted integrations, reason for updating, system and integration downtime during updating and a plan to roll-back the update if required must be submitted for approval prior to scheduling the updates.

    - A new secure backup of all system configuration files must be submitted to HU immediately after completion of a system update

  - Scheduled Work: Scheduled work must be performed during regular working hours, Monday through Friday, excluding holidays.

  - Emergency Service: The Owner will initiate service calls when the system is not functioning properly. Qualified personnel must be available to provide service to the complete system repair. The Owner must be furnished with a telephone number where the service supervisor can be reached at all times. Service personnel must be at site within 4 hours after receiving a request for service. The system must be restored to proper operating condition within 8 hours after service personnel arrive onsite.

  - Records and Logs: The Contractor must keep records and logs of each task, and must organize cumulative records for each component, and for the complete system chronologically. A continuous log must be maintained for all devices. The log must contain all initial settings. Complete logs must be kept and must be available for inspection on site, demonstrating that planned and systematic adjustments and repairs have been accomplished for the system.

  - Work Requests: The Contractor must separately record each service call request, as received. The form must include the serial number identifying the component involved, its location, date, and time the call was received, specific nature of trouble, names of service personnel assigned to the task, instructions describing what has to be done, the amount and nature of the material to be used, the time and date work started, and the time and date of completion. The Contractor must deliver a record of the work performed within 5 days after work is accomplished.

  - System Modifications: The Contractor must make any recommendations for system modification in writing to the Owner. System modifications must not be made without prior approval of the Owner. Any modifications made to the system must be incorporated into the operation and maintenance manuals, and other documentation affected.

    - A new secure backup of all system configuration files must be submitted to HU immediately after completion of a system update

    - The config files should be provided to HU via OThelp@harvard.edu

  - Spare Equipment:

    - Provide spare equipment where indicated in the [insert applicable section or equipment schedule appendix]

  - SERVICE LEVEL AGREEMENT (SLA)

    - The Contractor must provide with the bid a firm fixed pricing option(s) to provide continued warranty service and maintenance of the system for additional years two and three. The SLA must mirror that of the warranty and maintenance requirements during the warranty period as outlined in the Warranty and Maintenance articles above.

# Custom Software & Programming

- To avoid hardware becoming orphaned due to a manufacturer/vendor or integrator no longer providing the originally contracted services, it must be listed as a requirement in the system specifications to deliver the final systems firmware and software as part of the as-built package.

- The minimum software delivery and ownership language included in any specification sections defining systems integrations must be:

  - All software configuration files, firmware, graphics, user interface software elements, program files necessary to access or modify system configuration files and any custom programming furnished or installed as part of this scope of work must be submitted in native form to the Owner as part of the close-out package.

    - Refer to the secure submission requirements outlined above.

  - Where Ownership of any custom software, logic programming or other digital work product is stated in the specifications or executed agreements as being maintained by the Contractor or Vendor, the Contractor or Vendor must be required to extend to the Owner a perpetual license for use and modification of any custom software files when used with systems provided as part of this scope of work.

# Single Source of Truth

- To prevent incorrectly linked duplicate data values for an integration from being created, a single source of truth (SSOT) for each integration data type or parameter must be identified as part of the integration matrix.

- The SSOT must act as the only data repository for the selected data type where new values may be written. All other data repositories hosting the similar data type must be set as read only.

- Where possible, all systems utilizing a common data parameter must refer back to the SSOT for both read and write data access. The creation of daisy-chained systems interdependencies must be avoided.

  - Example: A room scheduling display should reference the main calendar host when creating or deleting room reservations and should not use an intermediate wayfinding or room management platform as a means to request or modify room calendar information.

# Integration Failure Modes

- An integration failure is any interruption or degradation in the integration such that the result impacts building functionality or user experience.

- The Specifying Engineer must identify the failure modes for each integration including the expected behavior of the integrated systems during an integration failure.

- The following design guidelines must be followed to minimize the potential functionality and user experience impacts of an integration failure:

  - No system must rely solely on the user interface or processing capabilities of another system to operate and must be able to operate basic functionality as a standalone platform

  - All systems must have the ability to for bi-directional communication with any integrated systems

  - All systems must be programmed to regularly poll for connection to other integrated systems

  - All systems must have the ability to maintain their current state in the event of a failure and no system must require the control automation of a separately integrated system for stable operation.

    - Example: If communication is lost to the building occupancy sensing platform, a lighting system must maintain the current light levels

  - All systems must be provided with a means to access user presets and typical system functions without requiring a separately integrated control interface.

    - Example: If a lighting system uses occupancy or the AV user interface for lighting preset recall it must be provided with a backup local preset controller directly connected to the lighting platform and able to be accessed by normal users in the event of a communications failure

# Life Safety and Code Compliance

- No systems servicing a life safety or code compliance functionality must be provided with an integration which is necessary to meet life safety or code requirements.

  - Exclusion: systems which are specifically engineered to meet NFPA standards using industry standard integrations, and which require no custom programming as part of a typical integration.

    - Example: Fire Command Center override of a sound masking or audiovisual system using a simple dry contact closure

  - All integrations to systems providing a life safety or code compliance functionality must be provided with the ability to test the integrity of the integration and provide automated alerts in the event of an integration failure

# Network Operations

The following network operations considerations should be addressed as part of the OT network specification

- Harvard University will passively monitor both the ICS/OT networks

- A backup of all ICS/OT systems will be done after commissioning and reviewed by the Business owner.

  - Refer to the secure submission requirements outlined above.

- Configuration changes which were made during commissioning will be removed if no longer needed

# Operation Technology / ICS Cybersecurity

- All devices and systems must be manufactured and configured to meet the Harvard University Security Systems Cyber Hardening Guidelines

  - Refer to the Requirements for Access to and Protection of the Harvard Network Contract Rider

- All ICS/OT Systems will follow the Harvard University Rider: Requirements for Access to and Protection of the Harvard Network.

- Harvard University follows the NIST CSF Cybersecurity framework or ISA/IEC 62443. All entities responsible for the specification, installation, maintenance, or operation of integrated systems must follow the process set forth in this framework including but not limited to:

  - ISA/IEC 62443-1-1: Security for Industrial Automation and Control Systems Part 1-1: Terminology, Concepts, and Models

  - ISA/IEC 62443-2-4: Security for Industrial Automation and Control Systems – Part 2-4: Security Program Requirements for IACS Service Providers

  - ISA/IEC 62443-4-2: Security for Industrial Automation and Control Systems: Technical Security Requirements for IACS Components

  - ISA/IEC 62443-4-1: Product Security Development Life-Cycle Requirements

  - ISA/IEC 62443-3-2:  Security Risk Assessment, System Partitioning, and Security Levels

  - ISA/IEC 62443-3-3: System Security Requirements and Security Levels

- All ICS/OT Systems vendors or integrators must fill out a Harvard University Information Security assessment through the assigned Harvard University business technical owner.

  - All changes or updates and upgrades approved and signed off by the business owner of the system and coordinated with HUIT-OT group when it involves any changes to the BMS Backend computing infrastructure and any software updates

- During the course of troubleshooting a commissioned piece of equipment, if there is a need for capturing the packets on the network, this work will be performed by a HUIT employee.

- All integrated equipment will utilize the latest version of SSH to access to locally if needed.  Telnet will not be used unless it has been approved by the Harvard University OT Steering committee

- ICS/OT Systems will not use modem connection for monitoring or access and are required to follow Rider: Requirements for Access to and Protection of the Harvard Network.

- Webservers on OT/ICS on devices will need to be turned disabled if not needed.  If needed vendor needs to justify the use in writing as part of the submittal process.

- There will be no wireless outbound connections to the Harvard network. All internal wireless connections between OT/ICS devices will need to be reviewed by Harvard University network and OT teams.

- All Bluetooth connections will be disabled and verified after commissioning by the Harvard University Business owner.

- No vendor will add a wireless AP to a device without consulting Harvard OT group.

# Vendor Provided Network Hardware

- In the event that due to the use of a proprietary network configuration, system bandwidth considerations or other mitigating factors it is determined that standalone network hardware or endpoint devices are required which will not be connected to the HU OT network: all submittal, commissioning, warrantee, service, demonstration and network cybersecurity requirements listed in this guideline will apply unless authorization to deviate from the requirements is provided in writing.

- ICS and OT Systems vendors who are responsible for their network equipment will follow the Rider: Requirements for Access to and Protection of the Harvard network.

- Vendors are required to supply inventory all network equipment conforming to the Network Coordination Submittal requirements listed previously.

- All ICS/OT Systems network equipment must have a formal support contract to perform quarterly patching and maintenance.  The contract will be provided to the business owner of the system on a yearly basis

- All integrated automation network equipment, when that approved integration uses an independent Ethernet switch within its solution skid or panel: that Ethernet switch must be of a type that allows management and port level mirroring for ease of troubleshooting of that system network without impacting the link between the equipment. The Span port will be assigned to a high thru-put port like 1Gb/s.

  - The switch will be powered with redundant power thru the panel’s/skid’s power/battery backup infrastructure. The switch will not be installed in a state that allows default access to its management and it will adhere to the Harvard’s OT security policy at the start of this document.

- All integrated network gateways will adhere to the Rider: Requirements for Access to and Protection of the Harvard Network.

  - They will be configured in a whitelisting setup, to only allow what is required thru the device between both sides. They will be configured to only accept this communication from approved devices. They will alert on non-compliant traffic and they will alert when a reset/startup/shutdown/reload is sent to devices on the protected side of the gateway.

  - Harvard preference is for Gateways to be able to send their logs to remote servers, where this isn’t feasible, and the product line has an option to log events locally to a flashcard then this card is required to have enough memory to last 6months of high volume alerts

  - ICS/OT vendors or integrators will need to provide inventory of all networks and devices behind the gateway as part of the submittal process outlined in the prior sections. This inventory will be reviewed by the Harvard University business owner.

# Vendor Provided Servers

- Where possible, attempts should be made to limit the use of on-premise servers or workstations. Where needed, these devices should be provided directly by HU. Where not possible due to proprietary or custom server requirements the following standards must be followed. Approval must be obtained from HUIT prior to specifying or deploying any third-party servers and workstations.

- Servers

  - Harvard requires all servers be housed in Harvard approved Datacenter.

  - Harvard requires all servers be virtualized.

  - Harvard’s supported guest server OS’s are RHEL 7.x,8.x and Windows server 2016, 2019.

  - Vendors are to provide the accurate specifications of the Hardware/Software requirements based on real world metrics (provided by the product vendors product management team and documented in the submittals)

  - If a vendor needs a field installed server, this needs to be approved and vetted by Harvard.

  - The field installed network connected server must follow the Harvard Enterprise Security policy (Link) and allow the installation of the following infrastructure that Harvard requires all servers to have installed and running.

    - CrowdStrike Agent

    - Splunk Agent

    - Anti-virus

    - Shavlik Agent

    - Nessus Agent

    - Networker Agent

    - Local firewall

  - Once installed HUIT is the only department that has the authority to configure/remove these agents.

  - OT/ICS vendors will not use self-signed certificates for access to their management systems from web interface.  All certificates will need to be signed by a trusted certificate authority == Got to be careful here are we going to create a sub-domain on HUIT CA or allow all end points reach out to external CA, Also not possible in the 2 tier model for connectivity within the “GREEN” network where we want the vendor to do the updates as we monitor that side of the networks.

- Vendor Provided Workstations – when required for system commissioning

  - If a workstation is required as part of commissioning/production, then this workstation is required to adhere to the OT/IT Standards.

  - This workstation needs to run the application as a non-administrative OS user.

  - The workstation is to have the following agents installed.

    - CrowdStrike Agent

    - Splunk Agent

    - Anti-virus

    - Shavlik Agent

    - Nessus Agent

    - Local firewall

  - The system is required to be backed up in some format to protect the project from a hardware failure which may lead to project timelines being missed.

  - The backup is required to be encrypted to protect against any lost.

- Workstations for system operation or management

  - All workstations required for regular systems operation or management must be provided by HU.

# Use of Wireless Communications to Support Integrations

- Non approved wireless connections should not be used to connect directly to by user devices or to other ICS/OT field controllers unless reviewed and approved by HU

- Wireless connections include:

  - Bluetooth Lower Energy (BLE) connections between OT sensors/controls and user mobile devices for setup or for normal operation

  - BLE connections between OT sensor/controls and the HUIT OT network wireless access points

  - BLE connections between one OT sensor/control and another of the same manufacturer for sub-system communications

  - Proprietary RF connections between one OT sensor/control and another of the same manufacturer for sub-system communications

  - RFID connection between an authentication/identification tag and an OT sensor

- Bluetooth connections for user peripherals

  - Where a Bluetooth connection is required for a user peripheral/HMI (keyboard, mouse, etc.), an initial auto/active discovery of up to two sets of peripherals must be completed and then auto/active discovery disabled.

- Approved wireless connections include:

  - Lutron Caseda

  - List others

  - Refer to Division 27 for additional approved wireless technologies

- Wireless frequency coordination

  - Submit a list of all required wireless frequencies to HUIT for approval as part of the submittal process

- Specifications must require that integrators confirm that the intended wireless frequencies are available for use and to be responsible for providing replacement hardware in an unobstructed frequency band if during testing it is determined that the intended frequency band is in use or that the provided equipment is obstructing communications by other systems intending to use the same band.

- No vendor will add a wireless AP to a device without consulting Harvard OT group.

# Remote Access

- Remote access to ICS/OT Network equipment will use Harvard University Site to Site VPN dedicated for Construction Projects.

- ICS/OT Vendors and integrators must not use cell service or wireless hotspots to remotely access any integrated automation network equipment such as Routers, Bridges, Switches, and hubs or any automation network devices and servers.

# Related Specification Sections

- Responsibility to related sections

  - The following list of specification sections should be included with any integration specification with the requirement to coordinate with the related sections

  - The specifying engineer

- Division 00 Procurement and Contracting Requirements

- Division 01 General Requirements

- Division 11 Equipment

  - Theatrical and Event Systems

  - Laboratory Equipment

- Division 13 Special Construction

  - Environmental Rooms/Chambers

  - Metal Building Systems

- Division 21

  - 210000 General Requirements Fire Protection

  - 210529 Hangers and Supports for Fire-Suppression Piping and Equipment

  - 210548 Vibration and Seismic Controls for Fire-Suppression Piping and Equipment

  - 210553 Identification for Fire-Suppression Piping and Equipment

  - 212200 Clean-Agent Fire-Extinguishing Systems

  - 213113 Electric-Drive, Centrifugal Fire Pumps

  - 213116 Diesel-Drive, Centrifugal Fire Pumps

  - 213213 Electric-Drive, Vertical-Turbine Fire Pumps

  - 213216 Diesel-Drive, Vertical-Turbine Fire Pumps

- Division 22

  - 220000 General Requirements for Plumbing

  - 220513 Common Motor Requirements for Plumbing Equipment

  - 220519 Meters and Gages for Plumbing Piping

  - 220529 Hangers and Supports for Plumbing Piping and Equipment

  - 220548 Vibration and Seismic Controls for Plumbing Piping and Equipment

  - 220553 Identification for Plumbing Piping and Equipment

  - 220963 Medical Gas Alarms

  - 221123.13 Domestic-Water Packaged Booster Pumps

  - 221223.11 Facility Indoor Potable-Water Storage Tanks

  - 221363 Facility Gray-Water Storage Tanks

  - 221519 General-Service Packaged Air Compressors and Receivers

  - 223200 Domestic Water Filtration Equipment

  - 223300 Electric, Domestic-Water Heaters

  - 223300 Electric, Domestic-Water Heaters

  - 226119 Compressed-Air Equipment for Laboratory and Healthcare Facilities

  - 226219 Vacuum Equipment for Laboratory and Healthcare Facilities

  - 226600 Chemical-Waste Systems for Laboratory and Healthcare Facilities

  - 226719 Processed Water Equipment for Laboratory and Healthcare Facilities

- Division 23 Heating, Ventilating, and Air Conditioning (HVAC)

  - 230000 General Requirements for HVAC

  - 230513 Common Motor Requirements for HVAC Equipment

  - 230519 Meters and Gauges for HVAC Piping

  - 230529 Hangers and Supports for HVAC Piping and Equipment

  - 230548 Vibration and Seismic Controls for HVAC

  - 230553 Identification for HVAC Piping and Equipment

  - 230923 Direct Digital Control (DDC) System for HVAC

  - 230993.11 Sequence of Operations for HVAC DDC

  - 231213 Facility Fuel-Oil Pumps

  - 232123 Hydronic Pumps

  - 232500 HVAC Water Treatment

  - 233813 Commercial-Kitchen Hoods

  - 235213 Electric Boilers

  - 235216 Condensing Boilers

  - 235223 Cast-Iron Boilers

  - 235233 Water-Tube Boilers

  - 235239 Fire-Tube Boilers

  - 235416.13 Gas-Fired Furnaces

  - 235416.16 Oil-Fired Furnaces

  - 236416 Centrifugal Water Chillers

  - 236423.13 Air-Cooled, Scroll Water Chillers

  - 236426.13 Air-Cooled, Rotary-Screw Water Chillers

  - 236426.16 Water-Cooled, Rotary-Screw Water Chillers

  - 236514.13 Open-Circuit, Induced-Draft, Counterflow Cooling Towers

  - 236514.14 Open-Circuit, Induced-Draft, Crossflow Cooling Towers

  - 236514.16 Closed-Circuit, Induced-Draft, Counterflow Cooling Towers

  - 236514.17 Closed-Circuit, Induced-Draft, Combined-Flow Cooling Towers

  - 237313.16 Indoor, Semi-Custom Air-Handling Units

  - 237313.19 Indoor, Custom Air-Handling Units

  - 237343.16 Outdoor, Semi-Custom Air-Handling Units

  - 237343.19 Outdoor, Custom Air-Handling Units

  - 237433 Dedicated Outdoor-Air Units

  - 238123.11 Small Capacity (6 Tons (21 kW) and Smaller), Computer-Room Air-Conditioners, Floor-Mounted Units

  - 238123.12 Large Capacity (7 Tons (25 kW) and Larger), Computer-Room Air-Conditioners, Floor-Mounted Units

  - 238123.13 Computer-Room Air-Conditioners, Ceiling-Mounted Units

  - 238123.18 Computer-Room, Rack-Cooling Equipment

  - 238129 Variable-Refrigerant-Flow HVAC Systems

  - 238413.29 Self-Contained Steam Humidifiers

- Division 26 Electrical

  - 260000 General Requirements for  Electrical

  - 260529 Hangers and Supports for Electrical Systems

  - 260548 Vibration and Seismic Controls for Electrical Systems

  - 260553 Identification for Electrical Systems

  - 260913 Electrical Power Monitoring

  - 260923 Lighting Control Devices

  - 260936 Modular Dimming Controls

  - 260943.16 Addressable Luminaire Lighting Controls

  - 260943.23 Relay-Based Lighting Controls

  - 261116.11 Secondary Unit Substations with Switchgear Secondary

  - 261116.12 Secondary Unit Substations with Switchboard Secondary

  - 261116.13 Secondary Unit Substations with Motor Control Center Secondary

  - 261323 Medium-Voltage Metal-Enclosed Switchgear

  - 261326 Medium-Voltage Metal-Clad Switchgear

  - 262413 Switchboards

  - 262416 Panelboards

  - 262416.16 Electronically Operated Circuit-Breaker Panelboards

  - 262419 Motor-Control Centers

  - 262713 Electricity Metering

  - 262733 Power Distribution Units

  - 262923 Variable-Frequency Motor Controllers

  - 262933  Controllers for Fire Pump Drivers

  - 263100 Photovoltaic Collectors

  - 263213.13 Diesel-Engine-Driven Generator Sets

  - 263213.16 Gas-Engine-Driven Generator Sets

  - 263353 Static Uninterruptible Power Supply

- Division 27 Communications

  - 270000	Communications General Conditions

  - 270200 Telecommunications Equipment Spaces

  - 270526 Grounding and Bonding for Communications Systems

  - 270528	Pathways for Communications Systems

  - 270543 Underground Ducts and Raceways for Outside Plant – Manhole & Conduit Systems

  - 270553 Identification for Communications Systems

  - 270600 Schedules for Communications Systems

  - 270800 Commissioning for Communications Systems

  - 271166 Communication Cabinets, Racks, Frames and Enclosures

  - 271119 Communication Termination Blocks and Patch Panels

  - 271123 Communication Cable Management and Ladder Rack

  - 271126 Communications Rack Mounted Power Protectors and Power Strips

  - 271313 Communication Copper Backbone Cabling

  - 271323 Communication Fiber Backbone Cabling

  - 271500.53 Antennas Communications Horizontal Cabling

  - 271513 Communication Copper Horizontal Cabling

  - 271543 Communications Faceplates and Connectors

  - 271619 Communications Patch Cords, Stations Cords, and Cross Connect Wires

  - 272133 Data Communications Wired and Wireless Data Network Connectivity

  - 272400 Data Communications Peripheral Data Equipment

  - 272500 Data Communications Software

  - 273223 Elevator Telephones

  - 273226 Ring-down Emergency Telephones

  - 274100	Audiovisual Systems

  - 275000 Distributed Communications and Monitoring Systems

- 280000	Electronic Safety and Security

  - 280000	Electronic Safety and Security

  - 280513 Conductors and Cables for Electronic Safety and Security

  - 280526 Grounding and Bonding for Security Systems

  - 280528 Pathway for Security Systems

  - 281300	Access Control

  - 281500 Security Communication

  - 282300	Video Surveillance

# Unique Specification Section Requirements

The following is a list of unique requirements per Division 25 specification sub-section (when required) but which are directly applicable to any specification section outlining a network based integration.

- 25 00 00 - Integrated Automation

  - A global 25 00 00 specification section may be utilized when a master systems integrator is required.

- 25 05 05 - Selective Demolition for Integrated Automation

  - When modifying an existing systems it is important for all to understand interconnectivity of the existing system before it is modified.

  - The Design Professional must coordinate existing conditions with appropriate Harvard University staff to verify impacts to the system and potential functional issues that will occur when the system is disrupted to accommodate planned modifications.

  - The Design Professional must document modifications to minimize impacts and loss of service.  If deemed necessary, installation must be documented in phases to minimize disruptions.

  - The Design Professional must review planned modifications with appropriate Harvard University staff for approval prior to releasing documents for bid purposes.

  - During bidding, the Construction Manager, General Contractor, Harvard University and Design Professional must verify that the competing contractors have the scope adequately covered within their bids.

  - Design documents must be updated and reissued to the successful contractor if modifications are discussed and agreed upon during the bidding phase.

- 25 05 13 - Conductors & Cables for Integrated Automation

  - Refer to the Harvard University Technology Standard Division 27.xxx.xxxx

- 25 05 28 - Pathways for Integrated Automation

  - Refer to the Harvard University Technology Standard Division 27.xxx.xxxx

- 25 05 28.29 - Hangers & Supports for Integrated Automation

  - Refer to the relevant Harvard University Technology Standard Specifications in Divisions 21, 22, 23, 26, 27 and 28.

  - When a common hanging system is utilized that will hold scope for multiple trades, it is necessary for one contractor to take responsibility for the structural integrity of the hanging system.

    - The Design Professional must determine which trade contractor must be responsible for the delegated design of the hangers and supports.

    - The primary contractor must be responsible for routing of their scope on the support system as well as the hanger and supports themselves.

    - The secondary contractors must be responsible to provide adequate information regarding their scope, such as size, spacing requirements, and linear weights.  Information must be provided to the primary contractor in a timely fashion.

    - The Design Professional must specify the contractor’s delegated design requirements, including necessity of a structural engineer to verify forces and loads into the building structure.

    - The Construction Manager or General Contractor must mange the coordination process in the field.

- 25 05 28.33 - Conduits & Backboxes for Integrated Automation

  - Refer to the Harvard University Technology Standard Division 27.xxx.xxxx

- 25 05 28.36 - Cable Trays for Integrated Automation

  - Refer to the Harvard University Technology Standard Division 27.xxx.xxxx

- 25 05 28.39 - Surface Raceways for Integrated Automation

  - Refer to Division 27.xxx.xxxx

- 25 05 48 - Vibration & Seismic Controls for Integrated Automation

  - Refer to the relevant Harvard University Technology Standard Specifications in Divisions 21, 22, 23, and 26.

  - The Design Professionals (Structural, Architecture, and MEP) must coordinate and document all relevant seismic and vibration criteria based upon minimum code requirements.  Design criteria must be listed on the architecture life safety/code drawing as well as in the relevant specification sections for each discipline.

  - For Data Centers or other sensitive facility types, the Design Professionals must coordinate with appropriate Harvard University staff to determine seismic and vibration criteria to be applied that exceed minimum code requirements.

- 25 05 53 - Identification for Integrated Automation

  - Refer to the relevant Harvard University Technology Standard Specifications in Divisions 21, 22, 23, 26, 27 and 28.

  - The Design Professional must coordinate with the appropriate Harvard University staff to verify identification requirements to be specified.

  - For existing systems that are modified, the Design professional must verify if the existing identification schemes must be applied or if a different scheme must be applied.

  - The Design professional must delineate requirements specific to each trade contractor and document within each relevant Division specification.

- 25 13 00 – Integrated Automation Control & Monitoring Network

  - Where required by HU operations, ICS/OT must have to be ability to send alarms to the building management system for warning, alarm, and system faults using the following preferred protocols to their latest published standard

    - Modbus/MSTP

    - Modbus/IP

    - BACnet/IP

    - BACnet/MSTP

- 25 15 00 - Integration Automation Software

  - Alarms will need to be reviewed and approved by Harvard University Business Owner and the Harvard University Operations Center.

  - The Design Professional must list all alarms being considered for review with the Harvard University Business Owner and the Harvard University Operations Center.  Final approved list must be included within the design documents.

  - Vendors must declare non-compliance or customization to standard protocols used within this space.

- 25 30 00 - Integrated Automation Instrumentation & Terminal Devices

  - Terminal devices include all equipment that are required to communicate with the integrated system, and may include environmental rooms, purified water equipment, dedicated laboratory control system, fan coil units, VAV devices, packaged air handling units, or emergency generators.

  - The Design Professional must determine which control and monitoring points will be communicated through the integrated system.

  - During the Design Phase, the Design Professional must coordinate with the terminal device manufacturers and confirm which points will be transmitted and the necessary communication protocols for each.

  - The Design Professional must confirm points to be communicated with the appropriate Harvard University staff.  Alarms must be reviewed and approved by Harvard University Business Owner and the Harvard University Operations Center.

  - Once confirmed, the Design Professional must specify points and communication protocols for each relevant terminal device.  Specification requirements must be provided for the system integrator (Division 25) as well as the relevant individual trade Division sections.  Specifications must clearly define responsibilities for each trade, including interconnection of communication and power between each trade.  The final communication check and testing must be the responsibility of the system integrator.

- 25 35 13 - Integration Automation Actuators & Operators

  - Actuators must be powered through the facility control system.  The Division 23 or 25 Contractor must be responsible for powering and wiring to each actuator.

  - Actuators must be selected to operate with 24VAC.  For actuators requiring higher torque, 120VAC may be considered.

    - The Design professional must develop specification requirements that assign the responsibility for 24 or 120 VAC to the Division 23 or 25 Contractor.

    - Note, this may require them to subcontract a Division 26 Contractor to wire 120 VAC actuators.

    - During the bidding process, the Construction Manager or General Contractor must verify that the Division 23 and/or 25 Contractor(s) have the required scope included.

  - Unless the actuator is small and unavailable with metal gears, gears must be hardened steel running in bronze, copper alloy or ball bearings.  Operator and gear trains must be totally enclosed in dustproof cast-iron, cast-steel or cast-aluminum housing.

  - Actuators must include manual indication of position.

  - Actuator failure positions must be indicated within control diagrams.

- 25 35 16 - Integration Automation Sensors & Transmitters

  - Size and selection of sensors must be based upon intended service and medium being measured.

  - Sensors must be located so that adequate readings will be obtained under all operating conditions.

    - The Design Professional must indicate location of all sensors on plan drawings to demonstrate proper location to the contract(s).

    - The Design Professional must verify sensors are appropriate for minimum and maximum flows, velocities, temperatures, etc. to which they will be exposed.

  - Accessories, such as thermowells must be utilized where appropriate.

- 25 35 19 - Integration Automation Control Valves

  - The Design Professional must indicate expected pressure drop through each control valve.  The pressure drop must be accounted for within pipe loss pressure calculations.

  - Butterfly style control valves must be high performance type.

- 25 35 23 - Integration Automation Control Dampers

  - Low leakage dampers must be utilized.  This must be applied to leakage through the damper frame and through the blades.  Bushings and seals must be included to minimize leakage out of the ductwork system.  Damper blade seals must be utilized to minimize leakage through the damper assembly when the blades are closed.

  - Parallel bladed dampers must be utilized for isolation (on/off) control applications.

  - Opposed blade dampers must be utilized for modulating control applications.

  - End switches must be utilized for determining damper position feedback.

- 25 35 26 - Integration Automation Compressed Air Supply

  - New devices must be selected as electronic.  Compressed air systems must not be provided for new construction unless approved by Harvard University.

  - When modifying facilities with existing automation compressed air systems, new control devices must be electronic unless installation of pneumatic devices is approved by Harvard University.

  - When modifying an existing compressed air system, the integrity of the system must be verified by Harvard University and the Design Professional during the design phase.

  - The Design Professional must coordinate existing conditions with appropriate Harvard University staff to verify impacts to the system and potential functional issues that will occur when the system is disrupted to accommodate planned modifications.

    - The Design Professional must document modifications to minimize impacts and loss of service.  If deemed necessary, installation must be documented in phases to minimize disruptions.

    - The Design Professional must review planned modifications with appropriate Harvard University staff for approval prior to releasing documents for bid purposes.

    - During bidding, the Construction Manager, General Contractor, Harvard University and Design Professional must verify that the competing contractors have the scope adequately covered within their bids.

    - Design documents must be updated and reissued to the successful contractor if modifications are discussed and agreed upon during the bidding phase.

- 25 50 00 - Integration Automation Facility Controls

  - The following building management systems are the preferred vendors for Harvard University. This includes buildings projects with a single building management platform requiring additional controls or partial retrofits. Any other building management system which is not listed below will need reviewed and approved by Harvard University’s Executive OT Steering Committee.

    - ENE Systems - Schneider Electric EcoStruxure

    - Siemens Desigo

  - If additional vendors will be considered for facility controls and/or system integrators, the Design Professional must review potential vendors early in the design phase with the appropriate Harvard University staff.  If deemed acceptable by the project team, the proposed vendor(s) must be submitted to Harvard University’s Executive OT Steering Committee for approval.

  - Design consultants and ICS/OT building management integrator or vendor will include the following:

  - Building Management system designs and installations for Harvard University under this specification must include the following:

    - The Building Management of the system must be based on an open implementation of BACnet using ASHRAE 135 published Standard (Link) as the communications protocol for communication between building management system and other ICS/OT hardware devices.

    - The building management system hardware and software must perform the control sequences as specified and shown in the design consultant’s control drawings and sequence of operation.

    - The engineering workstations or server must follow the Integrated Automation Network Servers workstation guideline and be able to run the software developed and tested by the manufacturer of the building management controllers.

    - Engineering workstations must conform to the B-OWS BACnet device profile, REST API or other Harvard approved secure communications protocol.

    - Approved must have access to all system points and graphic display screens, must be able to receive and acknowledge alarms, and must be able to control setpoints and other parameters based on their access credentials. All engineering work, such as trends, reports, that are accomplished from the engineering workstation must be available through Harvard University IT approved web-based interface (?)

    - The web-based interface must conform at a minimum to the B-OWS BACnet device profile and OWASP Application Security Verification Standard (ASVS) or similar BACnet B-BC HTML5 format

    - All building management filed panel must be connected using the standard ICS/OT protocols listed in 25.13.00

    - Control sequence logic for a system must reside in that system’s dedicated field level controller. The hardware in conjunction with the software residing on the controller must, where possible, execute the sequence of operation without relying on the building network.

    - The Building management system must be designed and installed such that Harvard University is able to perform repair, replacement, upgrades, and expansions of the system without further dependence on the original Building Management contractor.

    - Building management implementation documentation, configuration information, configuration tools, application programs (with comments explaining program logic), and other software used by the BMS must be licensed to and remain property of Harvard University

    - The building management system will interface with the preferred Building Analytics vendors:

      - Clockworks (formerly KGS)

      - Cimetrics

    - Any other Building Analytic vendors will need to be approved by the Harvard University’s Executive OT Steering Committee

  - The building management network must consist of a two-tier network. All Building panels will reside on the Harvard Building OT network (VLANS) Known a level 2.  All nonbuilding management panels such as (ICS/OT protocol gateways, routers switches and hubs) will reside on level 1 network.  Both networks will be monitored by Harvard University IT department (HUIT).

- The building management system must be an extension of the approved building management platforms listed above.

- The building management system must be capable of communication with the PI data historian. (Should we include this future use)

- In some cases, a multihomed connection spanning Level 1 and Level2 may be acceptable when matching existing Harvard standards or formally requested.

  - All network controllers and critical system controllers must be on UPS power. A critical system controller is defined as one that controls:

- Chilled Water, Hot Water, & Steam Generation and Distribution.

- Air Handlers (Supply AHUs, Make-up Air AHUs, Exhaust AHUs, Energy Recovery Units).

- Rooftop Units.

- Air Distribution for Critical Rooms: Labs, Vivariums, Executive Offices, HUIT data closets.

  - The UPS strategy can be designed and implemented as a small UPS per controller or one standalone UPS dedicated for the critical controls for an entire building. Additionally, a building UPS used for other systems may be used for the Building Management as well.

    - The UPS strategy must be identified as part of the design documents and specifications and validated with the project manager prior to completion of shop drawing submittals and procurement.

  - The UPS must be monitored by the Building Management System for “low battery” and “battery on” status.

  - Individual UPSs used for controllers will approved by the Harvard University Building manager. It will be mounted underneath the controller in an enclosure of similar specifications to the controller enclosure.

  - Design consultants and ICS/OT building management system vendors or integrator will use the requirements for any of the field devices referenced in 25 11 00 - Integrated Automation Network Devices

  - Other requirements of field controllers will consist of the following:

- Will be BACnet compatible and adhere to the BACnet protocol will use the latest ANSI/ASHRAE published Standard (Link)

- All field controllers must contain all the I/O and sequence logic for the system that they serve. For example, it is not acceptable to split an air handling unit between two field controllers.

- Airflow tracking control for a laboratory or vivarium must reside on one controller and not rely on the network to function.

- The hardware in conjunction with the software residing on the controller must execute the sequence of operation as specified. Controllers that contain “canned” programs which cannot be changed and do not meet the sequence of operations will not be acceptable.

- The hardware in conjunction with the software residing on the controller must, where possible, execute the sequence of operation without relying on the building network.

  - Building Management Ethernet Network Cable must be provided by the telecom contractor to a jack located inside the enclosure. Ethernet network cable must meet or exceed all requirements and will refer Harvard to University Division 27

  - Building Management System Enclosures include the following:

- Single keyed locking twistable knob(s).

- Tamper switch installed for Field devices which are deemed critical and alarm to the OPS CTR.

- Installation panels will be installed in secure area.  Not in a publicly accessible area.

- 25 58 01 - Integration Automation Control of Lighting Management System

  - The following lighting management systems are the preferred vendors for Harvard University. This includes buildings projects requiring additional controls or partial retrofits. Any other lighting management system chosen will need to be reviewed and approved by the Harvard University’s Executive OT Steering Committee.

    - Lutron

    - Wattstopper

    - Acuity/nLight

    - Legrand

  - Design consultants and Lighting Management Systems vendors or integrators will use the requirements for any of the field devices referenced in 25 10 00 - Integrated Automation Network Devices

  - Other requirements of field controllers will consist of the following:

    - Interconnections with the Lighting Management System will be BACnet compatible and adhere to the BACnet protocol will use the latest ANSI/ASHRAE published Standard (Link)

    - All other interconnections will other building systems will be wired connection unless reviewed by Harvard University IT Department (HUIT).

    - There will no direct access to the devices of the lighting system if remote access is needed

    - Vendors and integrators will follow the Harvard University Security Rider: Requirements for Access to and Protection of the Harvard Network.

    - SAS/Could analytics vendors will use outbound encrypted connection with no direct connection to the field level panels

    - No Control access will be permitted from a SAS or Cloud Services.

  - Lighting Management System requires a server to manage or backup system reference the Integrated Automation Network Servers section 25.11.13

  - The BMS vendor will a add a BACnet BMS panel to the Harvard Lighting network.

    - This panel will be configured as a BACnet Broadcast Management Device (BBMD). The panel on the BMS network will be the point of control/monitoring for lighting system, to allow single point of communication only to the objects or occupancy sensors needed.

    - All required/agreed upon objects or occupancy sensors will be programmed into this BMS network panel as foreign devices. These objects or sensors will then be viewable from the BMS.

    - There should be no cloud integration unless controls are put in place with the lighting control if there is an integrated to the building management system.

- 25 58 02 - Integration Automation Control of Photovoltaic (PV) Cells (Solar Panels)

  - The following Photovoltaic (PV) Cells (Solar Panels) are the preferred vendors for Harvard University. This includes buildings projects requiring additional controls or partial retrofits. Any other Photovoltaic (PV) Cells (Solar Panels) chosen will need to be reviewed and approved by the Harvard University’s Executive OT Steering Committee.

    - SolarEdge?

  - Design consultants and ICS/OT photovoltaic (PV) cells (solar panels) vendors or integrators will use the requirements for any of the field devices referenced in 25 10 00 - Integrated Automation Network Devices

  - Other requirements of field controllers for photovoltaic (PV) cells (solar panels) will consist of the following:

    - All other interconnections will be wired unless reviewed by Harvard University IT Department. (HUIT)

    - There will no direct access to the devices of the photovoltaic (PV) cells (Solar Panels) system if remote access is needed vendors and integrators will follow the Rider: Requirements for Access to and protection of the Harvard network. (Link)

    - SAS/Could analytics vendors will use outbound encrypted connection with no direct connection to the field level panels

    - No Control access will be permitted from a SAS or Cloud Services.

  - photovoltaic (PV) cells (solar panels) management system requires a server to manage or backup system reference the Integrated Automation Network Servers section 25.11.13

- 25 58 03  Integration Automation Control of Refrigeration Monitoring System

  - The following refrigeration systems are the preferred vendors for Harvard University. This includes buildings projects requiring additional controls or partial retrofits. Any other refrigeration systems chosen will need to be reviewed and approved by the Harvard University’s Executive OT Steering Committee.

    - National Resource Management (NRM) ?

  - Design consultants and Refrigeration Monitoring System vendors or integrators will use the requirements for any of the field devices referenced in 25 10 00 - Integrated Automation Network Devices

  - Other requirements of ICS/OT refrigeration systems vendors or integrators will include the following:

    - All other interconnections will be wired unless reviewed by Harvard University IT Department.

    - There will no direct access to the devices of the refrigeration systems if remote access is needed vendors and integrators will follow the Rider: Requirements for Access to and protection of the Harvard network.

    - SAS/Could analytics vendors will use outbound encrypted connection with no direct connection to the field level panels

    - No Control access will be permitted from a SAS or Cloud Services.

  - Refrigeration Monitoring Systems requiring a server to manage or backup system must refer to the Integrated Automation Network Servers section 25.11.13

- 25 58 04 - Integration Automation Control of Irrigation Monitoring System

  - The following Irrigation Monitoring Systems are the preferred vendors for Harvard University. This includes buildings projects requiring additional controls or partial retrofits. Any other irrigation systems chosen will need to be reviewed and approved by the Harvard University’s Executive OT Steering Committee.

    - Refer to approved systems list

  - Design consultants and Irrigation Monitoring Systems vendors or integrators will use the requirements for any of the field devices referenced in 25 10 00 - Integrated Automation Network Devices

  - Other requirements of Irrigation Monitoring Systems or integrators will include the following:

    - All other interconnections will be wired unless reviewed by Harvard University IT Department.

    - Interconnections with the irrigation system will be BACnet compatible and adhere to the BACnet protocol will use the latest ANSI/ASHRAE published Standard (Link)

    - There will no direct access to the devices of the irrigations systems if remote access is needed vendors and integrators will follow the Rider: Requirements for Access to and protection of the Harvard network. (Link)

    - SAS/Could analytics vendors will use outbound encrypted connection with no direct connection to the field level panels

    - No Control access will be permitted from a SAS or Cloud Services.

    - Irrigation systems requiring a server to manage or backup system reference the Integrated Automation Network Servers section 25.11.13

    - All system points and graphic display screens and alarms will be approved by the Harvard University Business Owner.

    - The irrigation system will be able to control setpoints and other parameters based on user access credentials.

End of Guidelines